## Cover
AVAADA · PowerTrain Optimizer
Data Centre Power Economics — Excel Report
Captive & Hybrid procurement · Tariff / PPA stacks · CFE & carbon
Field | Value
Project | Test
Study period | Jan–Dec 2026
Model version | 2.0.0
Generated | 24 Sep 2026, 11:32
Scope | Captive + Hybrid (equal analysis); DISCOM = savings baseline only
Viewpoint | DC buys Solar / Wind / BESS energy at fixed ₹/kWh — no plant CAPEX/MW
This model is a decision-support tool. Regulatory applicability, legal interpretation, commercial eligibility and final compliance requirements should be independently validated by the appropriate legal, regulatory and commercial advisors.

## Setup
1. Project setup snapshot
Parameter | Value
IT load (MW) | 250
PUE | 1.25
Peak load (MW) | 312.5
Load factor S1 (%) | 70
Storage tariff (₹/kWh) | 0
Cost blend basis | TARGET_POWER_PCT
Annual RE target (%) | 90
Hourly CFE target (%) | 90
CFE Pass rule | Every hour CFE% ≥ target (min hourly CFE ≥ target)
Captive mix G¦S¦W¦B (%) | 25.0¦35.0¦25.0¦15.0

## Comparison
2. Architecture comparison (Run Analysis)
DISCOM is baseline only. Captive and Hybrid are analysed equally.
Metric | DISCOM | CAPTIVE | HYBRID
Power cost (₹/kWh) | 9.539 | 2.7796 | 4.8855
Blended energy rate (₹/kWh) | 8.75 | 2.7733 | 4.6835
Annual bill (₹ Cr) | 1827.92 | 532.64 | 936.18
Savings vs DISCOM Y1 (₹ Cr) |  | 1145.28 | 779.24
NPV of savings (₹ Cr) |  | 16793.93 | 11749.88
Contracted RE / CFE mix (%) | 0 | 100 | 75
Target Grid (%) | 100 | 0 | 25
Target RE (%) | 0 | 100 | 75
Simulated Grid (%) | 25 | 0 | 25
Simulated RE (%) | 0 | 100 | 75
Hourly CFE min (%) | 0 | 15 | 11.3
Hourly CFE mean (%) | 0 | 57.7 | 52.2
Hours ≥ CFE target (%) | 0 | 29 | 26.7
Hourly CFE Pass/Fail | Fail | Fail | Fail
Annual RE Pass/Fail | Fail | Fail | Fail
Carbon saved (tCO₂) |  | 1571325 | 1178494
Annual load (MWh) | 1916250 | 1916250 | 1916250

## Captive
CAPTIVE — economics, mix & CFE
Item | Value
Power cost (₹/kWh) | 2.7796
Blended energy rate (₹/kWh) | 2.7733
DISCOM rate (₹/kWh) | 8.75
Solar stack (₹/kWh) | 4.16
Wind stack (₹/kWh) | 4.16
Storage tariff (₹/kWh) | 0
Grid % | 0
Solar % | 33.3333
Wind % | 33.3333
BESS % | 33.3334
RE / CFE mix % | 100
Target Grid ¦ RE % | 0.0 ¦ 100.0
Simulated Grid ¦ RE % | 0.0 ¦ 100.0
Cost blend basis | TARGET_POWER_PCT
Annual load (MWh) | 1916250
Annual bill (₹ Cr) | 532.6395
Savings vs DISCOM Y1 (₹ Cr) | 1145.2793
NPV of savings (₹ Cr) | 16793.9332
Carbon baseline (tCO₂) | 1571325
Carbon actual (tCO₂) | 0
Carbon saved (tCO₂) | 1571325
Hourly CFE min % | 15.0208
Hourly CFE mean % | 57.6883
Hours ≥ target % | 29.0183
Hourly CFE status | Fail
Annual RE % | 58.4334
Annual RE status | Fail
Tariff bill components
Bill component | Amount
Grid energy cost (₹) | 0
Solar energy cost (₹) | 2657197342.8
Wind energy cost (₹) | 2657197342.8
BESS / Storage cost (₹) | 0
Total energy cost (₹) | 5314394685.6
Monthly energy aggregates
month | month_index | load_mwh | solar_mwh | wind_mwh | direct_re_mwh | bess_charge_mwh | bess_discharge_mwh | grid_mwh | curtailment_mwh | re_pct | cfe_mean_pct
Jan | 1 | 162837.9533 | 44765.1691 | 40396.3339 | 81817.0816 | -3.0909e-13 | 0 | 0 | 3344.4214 | 50.2445 | 49.5321
Feb | 2 | 146997.6854 | 40892.906 | 36098.1303 | 73687.7586 | -1.7764e-13 | 0 | 0 | 3303.2776 | 50.1285 | 49.4157
Mar | 3 | 162732.3515 | 62435.8471 | 52360.0473 | 96998.4648 | -2.7001e-13 | 0 | 0 | 17797.4296 | 59.6061 | 58.3949
Apr | 4 | 157452.2622 | 60413.5939 | 50276.8225 | 93541.1217 | -1.7053e-13 | 0 | 0 | 17149.2946 | 59.4092 | 58.2028
May | 5 | 162837.9533 | 62787.5975 | 52828.73 | 97664.2521 | -2.2737e-13 | 0 | 0 | 17952.0754 | 59.9763 | 58.7803
Jun | 6 | 157452.2622 | 52703.9122 | 67729.0411 | 102467.6145 | -2.558e-13 | 0 | 0 | 17965.3388 | 65.0785 | 64.6552
Jul | 7 | 162732.3515 | 54271.9015 | 70532.8129 | 105652.2496 | -1.7408e-13 | 0 | 0 | 19152.4649 | 64.9239 | 64.4948
Aug | 8 | 162837.9533 | 54285.6002 | 70918.2885 | 106944.2329 | -2.2027e-13 | 0 | 0 | 18259.6558 | 65.6752 | 65.2576
Sep | 9 | 157346.6604 | 52443.1958 | 67999.7022 | 102488.7462 | -2.7711e-13 | 0 | 0 | 17954.1518 | 65.1356 | 64.7024
Oct | 10 | 162837.9533 | 55377.0139 | 45567.976 | 89912.1342 | -2.4514e-13 | 0 | 0 | 11032.8557 | 55.2157 | 54.4692
Nov | 11 | 157557.864 | 53121.8478 | 44344.55 | 87109.7929 | -2.4869e-13 | 0 | 0 | 10356.6049 | 55.2875 | 54.5455
Dec | 12 | 162626.7497 | 45250.7763 | 39696.9266 | 81446.6948 | -1.954e-13 | 0 | 0 | 3501.0081 | 50.082 | 49.3751

## Hybrid
HYBRID — economics, mix & CFE
Item | Value
Power cost (₹/kWh) | 4.8855
Blended energy rate (₹/kWh) | 4.6835
DISCOM rate (₹/kWh) | 8.75
Solar stack (₹/kWh) | 4.16
Wind stack (₹/kWh) | 4.16
Storage tariff (₹/kWh) | 0
Grid % | 25
Solar % | 35
Wind % | 25
BESS % | 15
RE / CFE mix % | 75
Target Grid ¦ RE % | 25.0 ¦ 75.0
Simulated Grid ¦ RE % | 25.0 ¦ 75.0
Cost blend basis | TARGET_POWER_PCT
Annual load (MWh) | 1916250
Annual bill (₹ Cr) | 936.1757
Savings vs DISCOM Y1 (₹ Cr) | 779.2431
NPV of savings (₹ Cr) | 11749.8795
Carbon baseline (tCO₂) | 1571325
Carbon actual (tCO₂) | 392831.25
Carbon saved (tCO₂) | 1178493.75
Hourly CFE min % | 11.2656
Hourly CFE mean % | 52.2388
Hours ≥ target % | 26.7466
Hourly CFE status | Fail
Annual RE % | 53.0473
Annual RE status | Fail
Tariff bill components
Bill component | Amount
Grid energy cost (₹) | 4191796875
Solar energy cost (₹) | 2790060000
Wind energy cost (₹) | 1992900000
BESS / Storage cost (₹) | 0
Total energy cost (₹) | 8974756875
Monthly energy aggregates
month | month_index | load_mwh | solar_mwh | wind_mwh | direct_re_mwh | bess_charge_mwh | bess_discharge_mwh | grid_mwh | curtailment_mwh | re_pct | cfe_mean_pct
Jan | 1 | 162837.9533 | 47003.4745 | 30297.2807 | 74744.9134 | -2.6645e-13 | 0 | 88093.0399 | 2555.8419 | 45.9014 | 45.1546
Feb | 2 | 146997.6854 | 42937.5942 | 27073.6248 | 67405.3325 | -1.5987e-13 | 0 | 79592.353 | 2605.8865 | 45.8547 | 45.1069
Mar | 3 | 162732.3515 | 65557.705 | 39270.0748 | 88913.9135 | -2.2027e-13 | 0 | 73818.438 | 15913.8663 | 54.6381 | 53.3192
Apr | 4 | 157452.2622 | 63434.3371 | 37707.6545 | 85787.1463 | -8.5265e-14 | 0 | 71665.1159 | 15354.8453 | 54.4845 | 53.1703
May | 5 | 162837.9533 | 65927.0433 | 39621.5871 | 89426.2099 | -1.1369e-13 | 0 | 73411.7433 | 16122.4204 | 54.9173 | 53.6092
Jun | 6 | 157452.2622 | 55339.1632 | 50796.8316 | 91625.086 | -2.0961e-13 | 0 | 65827.1762 | 14510.9088 | 58.1923 | 57.7125
Jul | 7 | 162732.3515 | 56985.5536 | 52899.6626 | 94605.1452 | -1.9895e-13 | 0 | 68127.2063 | 15280.071 | 58.1354 | 57.6503
Aug | 8 | 162837.9533 | 56999.9372 | 53188.7695 | 95520.349 | -2.4869e-13 | 0 | 67317.6042 | 14668.3577 | 58.6598 | 58.1838
Sep | 9 | 157346.6604 | 55065.4106 | 50999.8277 | 91642.2505 | -2.0961e-13 | 0 | 65704.4099 | 14422.9878 | 58.2423 | 57.7548
Oct | 10 | 162837.9533 | 58145.9228 | 34176.0162 | 82459.6637 | -2.3803e-13 | 0 | 80378.2896 | 9862.2753 | 50.6391 | 49.844
Nov | 11 | 157557.864 | 55777.996 | 33258.4458 | 79868.0594 | -2.8422e-13 | 0 | 77689.8046 | 9168.3824 | 50.6913 | 49.8995
Dec | 12 | 162626.7497 | 47513.3626 | 29772.7247 | 74521.1975 | -2.4158e-13 | 0 | 88105.5522 | 2764.8898 | 45.8235 | 45.08

## DISCOM_Baseline
DISCOM — economics, mix & CFE
Item | Value
Power cost (₹/kWh) | 9.539
Blended energy rate (₹/kWh) | 8.75
DISCOM rate (₹/kWh) | 8.75
Solar stack (₹/kWh) | 4.16
Wind stack (₹/kWh) | 4.16
Storage tariff (₹/kWh) | 0
Grid % | 100
Solar % | 0
Wind % | 0
BESS % | 0
RE / CFE mix % | 0
Target Grid ¦ RE % | 100.0 ¦ 0.0
Simulated Grid ¦ RE % | 25.0 ¦ 0.0
Cost blend basis | TARGET_POWER_PCT
Annual load (MWh) | 1916250
Annual bill (₹ Cr) | 1827.9188
Savings vs DISCOM Y1 (₹ Cr) | 0
NPV of savings (₹ Cr) | -22441.9279
Carbon baseline (tCO₂) | 1571325
Carbon actual (tCO₂) | 1571325
Carbon saved (tCO₂) | 0
Hourly CFE min % | 0
Hourly CFE mean % | 0
Hours ≥ target % | 0
Hourly CFE status | Fail
Annual RE % | 0
Annual RE status | Fail
Tariff bill components
Bill component | Amount
Grid energy cost (₹) | 16767187500
Solar energy cost (₹) | 0
Wind energy cost (₹) | 0
BESS / Storage cost (₹) | 0
Total energy cost (₹) | 16767187500
Monthly energy aggregates
month | month_index | load_mwh | solar_mwh | wind_mwh | direct_re_mwh | bess_charge_mwh | bess_discharge_mwh | grid_mwh | curtailment_mwh | re_pct | cfe_mean_pct
Jan | 1 | 162837.9533 | 0 | 0 | 0 | 0 | 0 | 162837.9533 | 0 | 0 | 0
Feb | 2 | 146997.6854 | 0 | 0 | 0 | 0 | 0 | 146997.6854 | 0 | 0 | 0
Mar | 3 | 162732.3515 | 0 | 0 | 0 | 0 | 0 | 162427.4263 | 0 | 0 | 0
Apr | 4 | 157452.2622 | 0 | 0 | 0 | 0 | 0 | 157161.1973 | 0 | 0 | 0
May | 5 | 162837.9533 | 0 | 0 | 0 | 0 | 0 | 162519.1679 | 0 | 0 | 0
Jun | 6 | 157452.2622 | 0 | 0 | 0 | 0 | 0 | 157452.2622 | 0 | 0 | 0
Jul | 7 | 162732.3515 | 0 | 0 | 0 | 0 | 0 | 162732.3515 | 0 | 0 | 0
Aug | 8 | 162837.9533 | 0 | 0 | 0 | 0 | 0 | 162837.9533 | 0 | 0 | 0
Sep | 9 | 157346.6604 | 0 | 0 | 0 | 0 | 0 | 157346.6604 | 0 | 0 | 0
Oct | 10 | 162837.9533 | 0 | 0 | 0 | 0 | 0 | 162837.9533 | 0 | 0 | 0
Nov | 11 | 157557.864 | 0 | 0 | 0 | 0 | 0 | 157557.864 | 0 | 0 | 0
Dec | 12 | 162626.7497 | 0 | 0 | 0 | 0 | 0 | 162626.7497 | 0 | 0 | 0

## Assumptions
Assumptions register (buyer-facing — plant leftovers excluded)
Parameter | Value | Unit | Source | Type | Description
general.project_name | Test |  | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | Display name for the demonstration project.
general.location | Maharashtra |  | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | Site location used only as a label. DISCOM naming in the concept note references MSEDCL.
general.currency | INR |  | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | Reporting currency. UI may display ₹ for INR.
general.study_start_month | 1 |  | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | Study period start month (1=Jan). Model hours = days in range × 24.
general.study_end_month | 12 |  | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | Study period end month (1=Jan … 12=Dec).
general.model_hours | 8760 | h | CALCULATED | CALCULATED | Normal-year hourly resolution required by the concept note. Leap years are not modelled in v1.
general.calendar_year | 2026 |  | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | Study year shown as 01 Jan – 31 Dec in the top bar. Choose any year 2020–2100. The hourly engine still runs 8,760 non-leap hours (29 Feb is not modelled).
general.re_curtailment_scope | Solar + Wind |  | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | Which renewable generation the curtailment % applies to: Solar only, Wind only, or Solar + Wind.
general.re_curtailment_pct | 0 | % of RE | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | Assumed / forced curtailment as a percentage of the selected RE scope (see RE curtailment scope). That share is removed before serving load or charging BESS. Additional curtailment can still occur if leftover RE cannot be absorbed. Editable input — not only a calculated KPI.
general.random_seed | 42 |  | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | Deterministic seed for synthetic solar/wind variability.
general.notes |  |  | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | Free-text project notes.
data_center.facility_name | Test |  | CALCULATED | CALCULATED | Same as General → Project name. Used on reports.
data_center.it_capacity_mw | 250 | MW | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | IT / critical load (MW). Same value drives Load → IT load and facility peak = IT × PUE.
data_center.grid_connection_kv | 220 | kV | CONCEPT_NOTE | CONCEPT_NOTE | Grid connection voltage stated in the concept note.
data_center.designated_consumer_status | Unknown / Legal Review Required |  | CONCEPT_NOTE | CONCEPT_NOTE | RCO designated-consumer status is not determined by this model. Concept note flags 220 kV SPV structure for legal review.
load.profile_source | SYNTHETIC |  | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | SYNTHETIC = parameterized generator. PROJECT DATA = imported hourly MW series (optional).
load.it_load_mw | 250 | MW | CALCULATED | CALCULATED | Same as Data Centre → IT capacity. Facility peak = IT Load × PUE.
load.pue | 1.25 | x | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | Power Usage Effectiveness. Total facility load = IT Load × PUE.
load.peak_load_mw | 312.5 | MW | CALCULATED | CALCULATED | Total facility load = it_load_mw × pue. Used for the hourly load profile over the study period.
load.load_factor_pct | 70 | % | CALCULATED | CALCULATED | Primary load factor (synced from Scenario 1). Actual average = Total load × LF. Run Analysis evaluates four LF scenarios in one pass.
load.load_factor_s1_pct | 70 | % | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | Load-factor scenario 1. Actual Load = Total load × LF. All four scenarios run in one analysis.
load.load_factor_s2_pct | 80 | % | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | Load-factor scenario 2. Actual Load = Total load × LF.
load.load_factor_s3_pct | 90 | % | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | Load-factor scenario 3. Actual Load = Total load × LF.
load.load_factor_s4_pct | 100 | % | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | Load-factor scenario 4. Actual Load = Total load × LF.
load.base_load_mw | 218.75 | MW | CALCULATED | CALCULATED | Actual average load = peak_load_mw × load_factor_pct / 100.
load.operating_hours | 8760 | h | CALCULATED | CALCULATED | Hours the load is considered online. Profile still has 8,760 steps; unused hours are zero if < 8760.
load.load_model | Seasonal TOD |  | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | How the hourly load shape is generated. Seasonal TOD is the default commercial path.
load.seasonal_tod_summer_months | 3,4,5 |  | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | Summer months (1–12, comma-separated) for Seasonal TOD shaping.
load.seasonal_tod_rainy_months | 6,7,8,9 |  | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | Rainy / monsoon months for Seasonal TOD shaping.
load.seasonal_tod_winter_months | 10,11,12,1,2 |  | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | Winter months for Seasonal TOD shaping.
load.seasonal_tod_day_start_hour | 8 | h | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | Day TOD start (hour 0–23). Default 8 = 8AM. Day band is start ≤ hour < end; night is the rest.
load.seasonal_tod_day_end_hour | 20 | h | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | Day TOD end exclusive (hour 0–23). Default 20 = 8PM. With start 8 → day 8AM–8PM, night 8PM–8AM.
load.seasonal_tod_summer_day | 1.05 | x | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | Summer day-band shape multiplier.
load.seasonal_tod_summer_night | 0.95 | x | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | Summer night-band shape multiplier.
load.seasonal_tod_rainy_day | 1.02 | x | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | Rainy day-band shape multiplier.
load.seasonal_tod_rainy_night | 0.98 | x | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | Rainy night-band shape multiplier.
load.seasonal_tod_winter_day | 1.03 | x | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | Winter day-band shape multiplier.
load.seasonal_tod_winter_night | 0.97 | x | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | Winter night-band shape multiplier.
load.weekday_multiplier | 1 | x | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | Weekday (Mon–Fri) shape multiplier before load-factor scaling.
load.weekend_multiplier | 0.98 | x | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | Weekend shape multiplier before load-factor scaling.
load.study_years | 1 | yr | CALCULATED | CALCULATED | Hourly engine always runs one 8,760-hour year. Financial model uses project life separately.
load.month_multiplier_1 | 1 | x | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | January load-shape multiplier.
load.month_multiplier_2 | 1 | x | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | February load-shape multiplier.
load.month_multiplier_3 | 1.01 | x | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | March load-shape multiplier.
load.month_multiplier_4 | 1.02 | x | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | April load-shape multiplier.
load.month_multiplier_5 | 1.03 | x | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | May load-shape multiplier.
load.month_multiplier_6 | 1.03 | x | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | June load-shape multiplier.
load.month_multiplier_7 | 1.02 | x | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | July load-shape multiplier.
load.month_multiplier_8 | 1.02 | x | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | August load-shape multiplier.
load.month_multiplier_9 | 1.01 | x | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | September load-shape multiplier.
load.month_multiplier_10 | 1 | x | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | October load-shape multiplier.
load.month_multiplier_11 | 0.99 | x | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | November load-shape multiplier.
load.month_multiplier_12 | 0.98 | x | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | December load-shape multiplier.
load.hour_multiplier_0 | 0.94 | x | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | Hour 00:00–00:59 diurnal multiplier before scaling.
load.hour_multiplier_1 | 0.93 | x | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | Hour 01:00–01:59 diurnal multiplier before scaling.
load.hour_multiplier_2 | 0.92 | x | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | Hour 02:00–02:59 diurnal multiplier before scaling.
load.hour_multiplier_3 | 0.92 | x | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | Hour 03:00–03:59 diurnal multiplier before scaling.
load.hour_multiplier_4 | 0.93 | x | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | Hour 04:00–04:59 diurnal multiplier before scaling.
load.hour_multiplier_5 | 0.95 | x | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | Hour 05:00–05:59 diurnal multiplier before scaling.
load.hour_multiplier_6 | 0.98 | x | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | Hour 06:00–06:59 diurnal multiplier before scaling.
load.hour_multiplier_7 | 1.02 | x | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | Hour 07:00–07:59 diurnal multiplier before scaling.
load.hour_multiplier_8 | 1.05 | x | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | Hour 08:00–08:59 diurnal multiplier before scaling.
load.hour_multiplier_9 | 1.06 | x | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | Hour 09:00–09:59 diurnal multiplier before scaling.
load.hour_multiplier_10 | 1.06 | x | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | Hour 10:00–10:59 diurnal multiplier before scaling.
load.hour_multiplier_11 | 1.05 | x | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | Hour 11:00–11:59 diurnal multiplier before scaling.
load.hour_multiplier_12 | 1.04 | x | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | Hour 12:00–12:59 diurnal multiplier before scaling.
load.hour_multiplier_13 | 1.05 | x | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | Hour 13:00–13:59 diurnal multiplier before scaling.
load.hour_multiplier_14 | 1.06 | x | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | Hour 14:00–14:59 diurnal multiplier before scaling.
load.hour_multiplier_15 | 1.06 | x | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | Hour 15:00–15:59 diurnal multiplier before scaling.
load.hour_multiplier_16 | 1.07 | x | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | Hour 16:00–16:59 diurnal multiplier before scaling.
load.hour_multiplier_17 | 1.08 | x | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | Hour 17:00–17:59 diurnal multiplier before scaling.
load.hour_multiplier_18 | 1.06 | x | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | Hour 18:00–18:59 diurnal multiplier before scaling.
load.hour_multiplier_19 | 1.02 | x | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | Hour 19:00–19:59 diurnal multiplier before scaling.
load.hour_multiplier_20 | 0.98 | x | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | Hour 20:00–20:59 diurnal multiplier before scaling.
load.hour_multiplier_21 | 0.96 | x | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | Hour 21:00–21:59 diurnal multiplier before scaling.
load.hour_multiplier_22 | 0.95 | x | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | Hour 22:00–22:59 diurnal multiplier before scaling.
load.hour_multiplier_23 | 0.94 | x | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | Hour 23:00–23:59 diurnal multiplier before scaling.
solar.profile_source | SYNTHETIC |  | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | SYNTHETIC = CF/diurnal generator. PROJECT DATA = imported 8,760 hourly MW series (optional).
solar.capacity_factor_pct | 22 | % | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | Target annual capacity factor used to scale the synthetic profile.
solar.sunrise_hour | 6 | h | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | Hour of day (0–24) at which generation becomes non-zero.
solar.sunset_hour | 18 | h | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | Hour of day at which generation returns to zero.
solar.peak_generation_hour | 12 | h | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | Hour of day of the diurnal peak.
solar.hourly_variability | 0.12 | frac | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | Deterministic relative noise amplitude applied in daylight hours.
solar.seasonal_winter | 0.8 | x | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | Solar seasonal factor for Winter (Dec–Feb).
solar.seasonal_summer | 1.11 | x | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | Solar seasonal factor for Summer (Mar–May).
solar.seasonal_monsoon | 0.96 | x | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | Solar seasonal factor for Monsoon (Jun–Sep).
solar.seasonal_post_monsoon | 0.98 | x | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | Solar seasonal factor for Post-monsoon (Oct–Nov).
wind.profile_source | SYNTHETIC |  | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | SYNTHETIC = CF/seasonal generator. PROJECT DATA = imported 8,760 hourly MW series (optional).
wind.capacity_factor_pct | 32 | % | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | Target annual capacity factor used to scale the synthetic profile.
wind.hourly_variability | 0.28 | frac | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | Deterministic relative noise amplitude for hourly wind.
wind.seasonal_winter | 0.72 | x | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | Wind seasonal factor for Winter (Dec–Feb).
wind.seasonal_summer | 0.95 | x | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | Wind seasonal factor for Summer (Mar–May).
wind.seasonal_monsoon | 1.28 | x | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | Wind seasonal factor for Monsoon (Jun–Sep).
wind.seasonal_post_monsoon | 0.83 | x | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | Wind seasonal factor for Post-monsoon (Oct–Nov).
grid.connection_voltage_kv | 220 | kV | CONCEPT_NOTE | CONCEPT_NOTE | Grid interconnection voltage from the concept note.
grid.energy_tariff_inr_per_kwh | 8.5 | ₹/kWh | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | Flat energy tariff if time-of-day is disabled.
grid.use_tod | TRUE |  | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | Apply peak/off-peak energy tariffs.
grid.tod_peak_start_hour | 18 | h | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | Start of peak TOD window.
grid.tod_peak_end_hour | 22 | h | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | End of peak TOD window (exclusive).
grid.tod_peak_tariff | 11 | ₹/kWh | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | Peak-window energy tariff.
grid.tod_offpeak_tariff | 7.5 | ₹/kWh | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | Off-peak energy tariff.
grid.demand_charge_inr_per_mw_month | 400000 | ₹/MW-month | CALCULATED | CALCULATED | Applied to the annual peak grid import.
grid.fixed_charge_inr_per_year | 12000000 | ₹/yr | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | Annual fixed grid/connection charge.
grid.transmission_inr_per_kwh | 0.4 | ₹/kWh | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | DISCOM / grid import transmission charge. Used when Network charges on grid is True.
grid.wheeling_inr_per_kwh | 0.3 | ₹/kWh | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | DISCOM / grid import wheeling charge. Used when Network charges on grid is True.
grid.banking_inr_per_kwh | 0.1 | ₹/kWh | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | Legacy banking unit rate (kept for Grid tab). RE banking uses commercial.re_banking_inr_per_kwh.
grid.other_charges_inr_per_kwh | 0.15 | ₹/kWh | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | DISCOM / grid import other volumetric charges. Used when Network charges on grid is True.
grid.loss_pct | 3 | % | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | Grid/network loss applied to wheeled RE in captive/OA structures.
grid.availability_pct | 99.5 | % | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | Deterministic availability: first (1-a)×8760 hours of each year are scaled; implemented as a constant derate of max import.
grid.tariff_escalation_pct | 4 | %/yr | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | Grid tariff escalation in the financial model.
grid.banking_enabled | FALSE |  | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | Legacy Grid-tab banking switch. RE banking uses commercial.re_banking_enabled.
grid.demand_charge_inr_per_kva_month | 400 | ₹/kVA-month | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | DISCOM demand charge (₹/kVA/month). Engine uses ₹/MW-month = this × 1,000.
grid.meter_rent_inr_per_month | 0 | ₹/month | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | Meter rent (monthly). Added to annual fixed grid cost × 12.
grid.liquidated_damages_inr_per_month | 0 | ₹/month | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | Liquidated damages / default charge (monthly). Added × 12 to annual fixed cost.
grid.power_factor | 0.95 | PU | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | Power factor (PU). Documentation / optional kVArh framing.
grid.kvarh_lagging_inr_per_kvarh | 0 | ₹/kVArh | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | kVArh charge for lagging PF (not auto-applied without reactive series).
grid.kvarh_leading_inr_per_kvarh | 0 | ₹/kVArh | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | kVArh surcharge for leading PF (not auto-applied without reactive series).
grid.grid_restricted | FALSE |  | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | Grid restricted flag (contract / operational constraint marker).
grid.excel_discom_energy_inr_per_kwh | 8.44 | ₹/kWh | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | DISCOM Energy Charges (base energy tariff).
grid.excel_discom_wheeling_inr_per_kwh | 0 | ₹/kWh | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | DISCOM Wheeling charges.
grid.excel_discom_tod_inr_per_kwh | -0.56 | ₹/kWh | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | DISCOM net TOD adjustment (peak extra − off-peak rebate; may be negative).
grid.excel_discom_ed_inr_per_kwh | 0.59 | ₹/kWh | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | DISCOM Electricity duty (₹/kWh).
grid.excel_discom_tose_inr_per_kwh | 0.28 | ₹/kWh | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | DISCOM TOSE / other statutory surcharge (₹/kWh).
grid.excel_discom_other_volumetric_inr_per_kwh | 0 | ₹/kWh | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | DISCOM other volumetric charges (FPPCA / misc ₹/kWh).
grid.excel_discom_total_inr_per_kwh | 8.75 | ₹/kWh | CALCULATED | CALCULATED | Total DISCOM = Energy + Wheeling + TOD + ED + TOSE + Other.
commercial.structure | HYBRID |  | CONCEPT_NOTE | CONCEPT_NOTE | Selected commercial structure. Hybrid is the primary optimisation architecture in the concept note.
commercial.include_discom | TRUE |  | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | Include DISCOM / grid supply in this architecture. For DISCOM structure this is always on. Selectable for HYBRID and OPEN ACCESS.
commercial.include_solar | TRUE |  | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | Include solar generation. Selectable for CAPTIVE, HYBRID and OPEN ACCESS. Off for DISCOM.
commercial.include_wind | TRUE |  | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | Include wind generation. Selectable for CAPTIVE, HYBRID and OPEN ACCESS. Off for DISCOM.
commercial.include_bess | TRUE |  | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | Include BESS. Selectable for CAPTIVE, HYBRID and OPEN ACCESS. Off for DISCOM.
commercial.cost_blend_basis | TARGET_POWER_PCT |  | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | CAPTIVE/HYBRID energy blend: TARGET_POWER_PCT = Architecture Percentage of power; SIMULATED_ENERGY_SHARE = same contracted Architecture mix % (DC buyer — suppliers deliver at fixed rates; no plant MW/MWh). Bill = mix % × DISCOM/Solar/Wind stacks + Storage tariff.
commercial.excel_solar_ppa_inr_per_kwh | 3.5 | ₹/kWh | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | Solar Energy Charges PPA (MH captive sample).
commercial.excel_solar_energy_inr_per_kwh | 0 | ₹/kWh | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | Energy Charges (Solar; usually 0 when PPA is used).
commercial.excel_solar_wheeling_inr_per_kwh | 0 | ₹/kWh | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | Wheeling (0 for EHV/STU captive; ~0.60 HT third-party).
commercial.excel_solar_transmission_inr_per_kwh | 0.5 | ₹/kWh | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | Transmission (MH RE OA sample ~0.49–0.50).
commercial.excel_solar_transmission_loss_inr_per_kwh | 0.11 | ₹/kWh | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | Transmission loss ₹/kWh proxy (~3.18% × PPA).
commercial.excel_solar_css_inr_per_kwh | 0 | ₹/kWh | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | CSS (0 for captive / GEOA exemption paths).
commercial.excel_solar_as_inr_per_kwh | 0 | ₹/kWh | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | Additional surcharge (0 for captive / GEOA + demand charges).
commercial.excel_solar_sldc_inr_per_kwh | 0.05 | ₹/kWh | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | SLDC volumetric proxy (actual often ₹/MW/day).
commercial.excel_solar_banking_inr_per_kwh | 0 | ₹/kWh | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | Banking ₹/kWh (MH GEOA is typically 8% in-kind).
commercial.excel_solar_ed_inr_per_kwh | 0 | ₹/kWh | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | Electricity duty on solar.
commercial.excel_solar_tose_inr_per_kwh | 0 | ₹/kWh | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | TOSE on solar.
commercial.excel_solar_total_inr_per_kwh | 4.16 | ₹/kWh | CALCULATED | CALCULATED | Sum of solar charge stack (PPA + charges).
commercial.excel_wind_ppa_inr_per_kwh | 3.5 | ₹/kWh | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | Wind Energy Charges PPA (MH captive sample).
commercial.excel_wind_energy_inr_per_kwh | 0 | ₹/kWh | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | Energy Charges (Wind).
commercial.excel_wind_wheeling_inr_per_kwh | 0 | ₹/kWh | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | Wheeling (0 for EHV/STU captive; ~0.60 HT third-party).
commercial.excel_wind_transmission_inr_per_kwh | 0.5 | ₹/kWh | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | Transmission (MH RE OA sample ~0.49–0.50).
commercial.excel_wind_transmission_loss_inr_per_kwh | 0.11 | ₹/kWh | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | Transmission loss ₹/kWh proxy (~3.18% × PPA).
commercial.excel_wind_css_inr_per_kwh | 0 | ₹/kWh | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | CSS (0 for captive / GEOA exemption paths).
commercial.excel_wind_as_inr_per_kwh | 0 | ₹/kWh | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | Additional surcharge (0 for captive / GEOA + demand charges).
commercial.excel_wind_sldc_inr_per_kwh | 0.05 | ₹/kWh | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | SLDC volumetric proxy (actual often ₹/MW/day).
commercial.excel_wind_banking_inr_per_kwh | 0 | ₹/kWh | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | Banking ₹/kWh (MH GEOA is typically 8% in-kind).
commercial.excel_wind_ed_inr_per_kwh | 0 | ₹/kWh | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | Electricity duty (Wind).
commercial.excel_wind_tose_inr_per_kwh | 0 | ₹/kWh | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | TOSE (Wind).
commercial.excel_wind_total_inr_per_kwh | 4.16 | ₹/kWh | CALCULATED | CALCULATED | Sum of wind charge stack.
commercial.excel_bess_ppa_inr_per_kwh | 0 | ₹/kWh | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | Storage tariff (₹/kWh) — consumer fixed rate for BESS % of power. No BESS CAPEX/OPEX; enter the contracted ₹/kWh.
commercial.excel_bess_energy_inr_per_kwh | 0 | ₹/kWh | CALCULATED | CALCULATED | Energy Charges (BESS). Captive/Hybrid: unused (0).
commercial.excel_bess_wheeling_inr_per_kwh | 0 | ₹/kWh | CALCULATED | CALCULATED | Wheeling (BESS). Not used for on-site Captive/Hybrid storage.
commercial.excel_bess_transmission_inr_per_kwh | 0 | ₹/kWh | CALCULATED | CALCULATED | Transmission (BESS). Not used for on-site Captive/Hybrid storage.
commercial.excel_bess_transmission_loss_inr_per_kwh | 0 | ₹/kWh | CALCULATED | CALCULATED | Transmission losses (BESS). Not used for Captive/Hybrid.
commercial.excel_bess_css_inr_per_kwh | 0 | ₹/kWh | CALCULATED | CALCULATED | CSS (BESS). Not used for on-site Captive/Hybrid storage.
commercial.excel_bess_as_inr_per_kwh | 0 | ₹/kWh | CALCULATED | CALCULATED | Additional surcharge (BESS). Not used for Captive/Hybrid.
commercial.excel_bess_sldc_inr_per_kwh | 0 | ₹/kWh | CALCULATED | CALCULATED | SLDC (BESS). Not used for Captive/Hybrid.
commercial.excel_bess_banking_inr_per_kwh | 0 | ₹/kWh | CALCULATED | CALCULATED | Banking (BESS). Not used for Captive/Hybrid.
commercial.excel_bess_ed_inr_per_kwh | 0 | ₹/kWh | CALCULATED | CALCULATED | Electricity duty (BESS). Not used for Captive/Hybrid.
commercial.excel_bess_tose_inr_per_kwh | 0 | ₹/kWh | CALCULATED | CALCULATED | TOSE (BESS). Not used for Captive/Hybrid.
commercial.excel_bess_total_inr_per_kwh | 0 | ₹/kWh | CALCULATED | CALCULATED | Captive/Hybrid: equals Storage tariff. Open Access: sum of BESS charge stack.
commercial.mix_discom_pct | 25 | % | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | DISCOM/grid share of Architecture Percentage of power (HYBRID). Selected assets’ mix % must sum to 100. Pricing share only.
commercial.mix_solar_pct | 35 | % | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | Solar share of Architecture Percentage of power (CAPTIVE / HYBRID). Selected assets’ mix % must sum to 100. Pricing / energy-contract share.
commercial.mix_wind_pct | 25 | % | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | Wind share of Architecture Percentage of power (CAPTIVE / HYBRID). Selected assets’ mix % must sum to 100. Pricing / energy-contract share.
commercial.mix_bess_pct | 15 | % | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | BESS share of contracted Architecture energy (CAPTIVE / HYBRID). Priced at Storage tariff ₹/kWh — not a plant MW/MWh size. Selected assets’ mix % must sum to 100.
commercial.grid_power_pct | 25 | % | CALCULATED | CALCULATED | Alias of DISCOM / grid mix % (synced from mix_discom_pct when DISCOM is included).
commercial.captive_re_pct | 75 | % | CALCULATED | CALCULATED | Alias of RE mix % = Solar + Wind + BESS selected shares (synced on recompute).
commercial.discom_name | MSEDCL |  | CONCEPT_NOTE | CONCEPT_NOTE | DISCOM counterparty name referenced in the concept note DISCOM structure.
commercial.captive_ownership_pct | 26 | % | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | Captive ownership share. Not a legal qualification test.
commercial.captive_allocation_pct | 100 | % | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | Share of RE project output allocated to this data centre.
commercial.captive_energy_price | 3.8 | ₹/kWh | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | Captive delivered energy price before network charges.
commercial.oa_energy_price | 4.2 | ₹/kWh | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | Open-access RE energy price before OA charges.
commercial.apply_network_charges_to_re | TRUE |  | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | Legacy combined RE network flag (migrated into Solar / Wind flags). Kept for older projects.
commercial.apply_network_charges_to_solar | TRUE |  | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | Apply Solar-specific transmission/wheeling/banking/other charges to annual solar generation.
commercial.apply_network_charges_to_wind | TRUE |  | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | Apply Wind-specific transmission/wheeling/banking/other charges to annual wind generation.
commercial.apply_network_charges_to_bess | FALSE |  | CALCULATED | CALCULATED | BESS network charges on discharge. Forced off for Captive/Hybrid (use Storage tariff ₹/kWh).
commercial.apply_network_charges_to_grid | FALSE |  | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | Apply DISCOM/grid-specific transmission/wheeling/other charges to grid import in addition to the energy tariff.
commercial.re_transmission_inr_per_kwh | 0.4 | ₹/kWh | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | Legacy combined RE transmission rate (migrated into Solar / Wind rates).
commercial.re_wheeling_inr_per_kwh | 0.3 | ₹/kWh | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | Legacy combined RE wheeling rate.
commercial.re_other_charges_inr_per_kwh | 0.15 | ₹/kWh | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | Legacy combined RE other volumetric rate.
commercial.re_banking_enabled | FALSE |  | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | Legacy combined RE banking switch.
commercial.re_banking_inr_per_kwh | 0.1 | ₹/kWh | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | Legacy combined RE banking rate.
commercial.solar_transmission_inr_per_kwh | 0.4 | ₹/kWh | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | Solar network transmission charge. Independent of Wind and DISCOM rates.
commercial.solar_wheeling_inr_per_kwh | 0.3 | ₹/kWh | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | Solar network wheeling charge. Independent of Wind and DISCOM rates.
commercial.solar_other_charges_inr_per_kwh | 0.15 | ₹/kWh | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | Solar other volumetric network charges.
commercial.solar_banking_enabled | FALSE |  | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | If false, Solar banking charges are zero regardless of the Solar banking unit rate.
commercial.solar_banking_inr_per_kwh | 0.1 | ₹/kWh | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | Solar banking-related charge. Applied only when Solar banking is enabled.
commercial.wind_transmission_inr_per_kwh | 0.4 | ₹/kWh | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | Wind network transmission charge. Independent of Solar and DISCOM rates.
commercial.wind_wheeling_inr_per_kwh | 0.3 | ₹/kWh | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | Wind network wheeling charge. Independent of Solar and DISCOM rates.
commercial.wind_other_charges_inr_per_kwh | 0.15 | ₹/kWh | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | Wind other volumetric network charges.
commercial.wind_banking_enabled | FALSE |  | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | If false, Wind banking charges are zero regardless of the Wind banking unit rate.
commercial.wind_banking_inr_per_kwh | 0.1 | ₹/kWh | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | Wind banking-related charge. Applied only when Wind banking is enabled.
commercial.bess_transmission_inr_per_kwh | 0.4 | ₹/kWh | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | BESS network transmission charge on discharge energy. Independent of Solar / Wind / DISCOM rates.
commercial.bess_wheeling_inr_per_kwh | 0.3 | ₹/kWh | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | BESS network wheeling charge on discharge energy.
commercial.bess_other_charges_inr_per_kwh | 0.15 | ₹/kWh | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | BESS other volumetric network charges on discharge energy.
commercial.bess_banking_enabled | FALSE |  | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | If false, BESS banking charges are zero regardless of the BESS banking unit rate.
commercial.bess_banking_inr_per_kwh | 0.1 | ₹/kWh | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | BESS banking-related charge. Applied only when BESS banking is enabled.
compliance.rpo_rco_applicability | Unknown / Legal Review Required |  | CONCEPT_NOTE | CONCEPT_NOTE | Integrated RPO/RCO applicability (purchase + consumption obligation). User-declared — the model does not infer it.
compliance.rpo_rco_target_pct | 0 | % | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | Integrated RPO/RCO target (% of DC load that must be met from RE). One target covers both Renewable Purchase and Consumption Obligation.
compliance.rpo_rco_compliance_route | Buyout |  | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | How shortfall is costed if Applicable (Buyout or REC).
compliance.rpo_rco_buyout_inr_per_kwh | 1 | ₹/kWh | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | RPO/RCO shortfall buyout cost when route is Buyout (or not REC).
compliance.rpo_rco_rec_inr_per_kwh | 1 | ₹/kWh | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | REC cost used when RPO/RCO compliance route is REC.
compliance.eso_applicability | Unknown / Legal Review Required |  | CONCEPT_NOTE | CONCEPT_NOTE | ESO applicability is user-declared.
compliance.eso_target_pct | 2.5 | % | CONCEPT_NOTE | CONCEPT_NOTE | Single ESO storage obligation target (% of annual DC load).
compliance.eso_re_origin_min_pct | 85 | % | CONCEPT_NOTE | CONCEPT_NOTE | Minimum renewable-origin share of stored energy under the ESO requirement.
compliance.eso_buyout_inr_per_kwh | 1.2 | ₹/kWh | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | ESO shortfall / origin-failure cost if applicable.
compliance.annual_re_target_pct | 90 | % | CONCEPT_NOTE | CONCEPT_NOTE | Selected annual RE / Architecture CFE mix target.
compliance.hourly_cfe_target_pct | 90 | % | CONCEPT_NOTE | CONCEPT_NOTE | 24×7 CFE target. Pass = every hour’s CFE% from Min(Load, Solar+Wind+CF-BESS)/Load × 100 meets this target; otherwise Fail.
compliance.grid_emission_factor_tco2_per_mwh | 0.82 | tCO2/MWh | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | Grid emission factor for carbon accounting (baseline and DISCOM share).
financial.project_life_yr | 25 | yr | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | Cash-flow horizon.
financial.discount_rate_pct | 10 | % | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | Real/nominal discount rate applied to cash flows as entered (no separate real/nominal conversion).
financial.electricity_escalation_pct | 4 | % | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | Grid energy-cost escalation.
financial.re_cost_escalation_pct | 2 | % | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | RE tariff/OPEX escalation where billed as energy.
financial.tax_pct | 0 | % | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | Optional tax on taxable income. Default 0 (pre-tax).
financial.additional_costs | [] | ₹/yr | DEFAULT_ASSUMPTION | DEFAULT_ASSUMPTION | User-defined additional annual cost line items (label + amount). Included in delivered ₹/kWh and cashflows.

## Methodology
Methodology (commercial buyer)
Topic | Rule
Bill | Annual load × blended ₹/kWh (+ demand/fixed/compliance if configured)
Blended ₹/kWh | Discom×G% + Solar×S% + Wind×W% + Storage×B% (Architecture mix)
Savings vs DISCOM | 100% DISCOM bill − architecture bill (Year 1)
NPV of savings | PV of yearly bill savings over project life at discount rate (no plant CAPEX)
BESS | Storage tariff ₹/kWh only — no plant MW/MWh
Hourly CFE Pass | Min hourly CFE ≥ target and 100% of hours ≥ target
Hourly CFE formula | Min(Load, Solar+Wind+CF-origin BESS) / Load × 100
Target vs Simulated | Both = Architecture contracted mix % on the buyer path
This model is a decision-support tool. Regulatory applicability, legal interpretation, commercial eligibility and final compliance requirements should be independently validated by the appropriate legal, regulatory and commercial advisors.